## Cover Page
OS-DORAEN ¦
ELECTRICAL ENGINEERING • CABLE SIZING AUTOMATION
CABLE SIZING & SELECTION
Electrical Design • Current Capacity • Voltage Drop • Short-Circuit Checks
PROJECT & DOCUMENT CONTROL
Project / Plant Name | Enter project name | Client / Organization | Enter client name
Project Location | Enter site / location | System / Panel | Cable sizing study
Document Number | OSD-CBL-AUTO-001 | Revision Number | Rev. 00
Document Status | For Review | Issue Date | 21-Oct-2026
Prepared By | Enter name / designation | Checked By | Enter name / designation
Approved By | Enter name / designation | Approval Date | Enter date
WORKBOOK CONTENTS
Select a worksheet name below to open the relevant cable sizing section.
OS-DORAEN | Open worksheet | Bulk Calculator | Open worksheet
Bulk Instructions | Open worksheet | Motor Calculation | Open worksheet
Cable Data | Open worksheet | Formula Guide | Open worksheet
Design Notes | Open worksheet | Lists | Open worksheet
Cable Data Master | Open worksheet | AUTO ENGINE | Open worksheet
QA Release Notes | Open worksheet
DOCUMENT NOTES
This workbook is a calculation aid. Verify cable installation method, ambient and grouping derating, conductor material, insulation rating, protective-device coordination, voltage-drop limits, and short-circuit withstand against applicable standards and project requirements before approval.

## OS-DORAEN
OS-DORAEN — ENGINEERING AUTOMATION
VOLUME 3 ¦ AUTOMATIC CABLE SIZING & PROTECTION REVIEW
DESIGN CONTROL INPUTS
Maximum running voltage drop (%) | 2.5
Maximum starting voltage drop (%) | 10
Cable selection method | Smallest standard cable size passing current + starting VD + running VD + cable SC
Short-circuit method | Transformer kVA + LV voltage + nameplate Z% → prospective 3-phase SC
IMPORTANT | Enter yellow inputs in Bulk Calculator. Cable size is automatic. Transformer Z% and CB Icu/Ics are engineering inputs and must be verified.
SYNCHRONIZED BULK RESULTS
Sr. No. | Equipment / Tag | Motor kW | Starting Method | Runs | AUTO Cable Size (mm²) | Cable Construction | FLC (A) | Derated Capacity (A) | Starting VD % | Running VD % | Cable SC Check | FINAL CABLE RESULT
1 | Motor | 150 | VFD | 2 | 120 | 3C / Al / XLPE / Armoured | 257.3447 | 272.42 | 0.80321 | 1.0123 | PASS | SUITABLE
2 | Motor | 11 | Star-Delta | 2 | 25 | 3C / Al / XLPE / Armoured | 18.8719 | 101.76 | 0.1908 | 0.31927 | PASS | SUITABLE
3 | Motor | 110 | Star-Delta | 2 | 70 | 3C / Al / XLPE / Armoured | 188.7194 | 189.74 | 0.43162 | 0.61733 | PASS | SUITABLE
4 | Motor | 13 | VFD | 1 | 25 | 3C / Al / XLPE / Armoured | 22.3032 | 50.88 | 0.22549 | 0.37731 | PASS | SUITABLE
5 | Motor | 55 | Star-Delta | 2 | 50 | 3C / Al / XLPE / Armoured | 94.3597 | 150.52 | 0.94637 | 1.4534 | PASS | SUITABLE
6 | Motor | 70 | VFD | 2 | 35 | 3C / Al / XLPE / Armoured | 120.0942 | 124.02 | 0.92322 | 1.4821 | PASS | SUITABLE
7 | Motor | 110 | VFD | 1 | 240 | 3C / Al / XLPE / Armoured | 188.7194 | 211.47 | 0.8314 | 0.82999 | PASS | SUITABLE
8 | Screen | 3.7 | DOL | 1 | 70 | 4C / Al / XLPE / Armoured | 7.6966 | 91.69 | 0.070412 | 0.092699 | PASS | SUITABLE
9 | Dissolved Air Generator | 22 | Star-Delta | 2 | 25 | 3C / Al / XLPE / Armoured | 44.1031 | 101.76 | 0.0077102 | 0.012222 | PASS | SUITABLE
10 | Air Compressor | 5.5 | DOL | 1 | 25 | 3C / Cu / XLPE / Unarmoured | 12.404 | 63.6 | 0.0028626 | 0.0042539 | PASS | SUITABLE
11 | DAF Rake Mechanism | 1.1 | VFD | 1 | 25 | 3C / Cu / XLPE / Unarmoured | 2.2052 | 63.6 | 0.00050891 | 0.00075625 | PASS | SUITABLE
12 | Air Dryer | 0.3 | Direct/Non-Motor | 1 | 25 | 3C / Cu / XLPE / Unarmoured | 2.038 | 63.6 | 0.000818 | 0.0012155 | PASS | SUITABLE
13 | Auto drain vavle - 01 | 0.05 | Direct/Non-Motor | 1 | 25 | 3C / Al / XLPE / Armoured | 0.33967 | 50.88 | 0.00020655 | 0.00032742 | PASS | SUITABLE
14 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
15 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
16 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
17 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
18 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
19 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS
20 | 0 | 0 | VFD | 1 |  | 3C / Al / XLPE / Armoured | 0 | 0 | 0 | 0 | PASS

## Bulk Calculator
OS-DORAEN — VOLUME 3 ¦ AUTOMATIC BULK CABLE SIZING & PROTECTION REVIEW
YELLOW = USER INPUT ¦ GREEN = AUTOMATIC ¦ Cable size is never entered manually ¦ Transformer Z% = nameplate input ¦ CB Icu/Ics = manufacturer input
Sr. No. | Equipment / Tag | Transformer Selected KVA | Transformer Z% INPUT | Motor kW | METHOD OF STARTING | AUTO CABLE SIZE mm² | Cable Construction (INPUT) | OD (AUTO) | No. of Runs (INPUT) | Voltage V | Derating Factor | Running PF | Efficiency η | Cable Length km | Starting Multiplier | Starting PF | Prospective SC kA (AUTO) | Fault Time s | k Factor (AUTO) | FLC A | Cable Rating in Air A (AUTO) | R Ω/km | X Ω/km | Derated Capacity A | Capacity Check | Starting Current A | Starting Sinθ | Starting Impedance Ω | Starting VD V | Starting VD % | Starting VD Check | Running Sinθ | Running Impedance Ω | Running VD V | Running VD % | Running VD Check | Min. SC Area mm² | Actual Cable Area mm² | Cable SC Withstand kA | SC Check | FINAL CABLE RESULT | REQUIRED POLES | CB Family | Total Design Current A | Selected Standard CB Rating A | Trip Unit Basis | Thermal/Overload Setting Target A | Magnetic/Instantaneous Basis | Starting Withstand Check | Cable Coordination Check | FINAL CB SELECTION | CB Icu/Ics INPUT kA | CB Short-Circuit Check | Short-Circuit Design Note | MCCB Selection Check | Type | Cores | Material | Insulation | Armour | Size (AUTO) | VD Ref (AUTO) | OD (AUTO) | Ampacity (AUTO) | R (AUTO) | X (AUTO) | kSC (AUTO) | Not Found | Select Type, Cores, Material, Insulation, Armour and Size. Ampacity, R, X and k_SC are automatic.
1 | Motor | 400 | 4.5 | 150 | VFD | 120 | 3C / Al / XLPE / Armoured | 31 | 2 | 415 | 0.53 | 0.85 | 0.954 | 0.06 | 1.5 | 0.3 | 12.3663 | 1 | 143 | 257.3447 | 257 | 0.325 | 0.072 | 272.42 | PASS | 386.0171 | 0.95394 | 0.083092 | 3.3333 | 0.80321 | PASS | 0.52678 | 0.15709 | 4.2012 | 1.0123 | PASS | 86.4774 | 240 | 34.32 | PASS | SUITABLE | 3 | MCCB | 257.3 | 320 | Manufacturer-specific adjustable trip unit | 257.3 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 320 A MCCB; target Ir 257.3 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 12.37 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 120 | 0.325 | 31 | 257 | 0.325 | 0.072 | 143
2 | Motor | 100 | 4.5 | 11 | Star-Delta | 25 | 3C / Al / XLPE / Armoured | 17.5 | 2 | 415 | 0.53 | 0.85 | 0.954 | 0.06 | 1.5 | 0.3 | 3.0916 | 1 | 143 | 18.8719 | 96 | 1.54 | 0.08 | 101.76 | PASS | 28.3079 | 0.95394 | 0.26916 | 0.79182 | 0.1908 | PASS | 0.52678 | 0.67557 | 1.325 | 0.31927 | PASS | 21.6194 | 50 | 7.15 | PASS | SUITABLE | 3 | MCCB | 18.9 | 20 | Manufacturer-specific adjustable trip unit | 18.9 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 20 A MCCB; target Ir 18.9 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 3.09 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 25 | 1.54 | 17.5 | 96 | 1.54 | 0.08 | 143
3 | Motor | 400 | 4.5 | 110 | Star-Delta | 70 | 3C / Al / XLPE / Armoured | 25 | 2 | 415 | 0.53 | 0.85 | 0.954 | 0.03 | 1.5 | 0.3 | 12.3663 | 1 | 143 | 188.7194 | 179 | 0.567 | 0.077 | 189.74 | PASS | 283.0792 | 0.95394 | 0.12178 | 1.7912 | 0.43162 | PASS | 0.52678 | 0.26126 | 2.5619 | 0.61733 | PASS | 86.4774 | 140 | 20.02 | PASS | SUITABLE | 3 | MCCB | 188.7 | 200 | Manufacturer-specific adjustable trip unit | 188.7 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 200 A MCCB; target Ir 188.7 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 12.37 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 70 | 0.567 | 25 | 179 | 0.567 | 0.077 | 143
4 | Motor | 100 | 4.5 | 13 | VFD | 25 | 3C / Al / XLPE / Armoured | 17.5 | 1 | 415 | 0.53 | 0.85 | 0.954 | 0.03 | 1.5 | 0.3 | 3.0916 | 1 | 143 | 22.3032 | 96 | 1.54 | 0.08 | 50.88 | PASS | 33.4548 | 0.95394 | 0.53832 | 0.93579 | 0.22549 | PASS | 0.52678 | 1.3511 | 1.5659 | 0.37731 | PASS | 21.6194 | 25 | 3.575 | PASS | SUITABLE | 3 | MCCB | 22.3 | 25 | Manufacturer-specific adjustable trip unit | 22.3 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 25 A MCCB; target Ir 22.3 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 3.09 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 25 | 1.54 | 17.5 | 96 | 1.54 | 0.08 | 143
5 | Motor | 400 | 4.5 | 55 | Star-Delta | 50 | 3C / Al / XLPE / Armoured | 22 | 2 | 415 | 0.53 | 0.85 | 0.954 | 0.1 | 1.5 | 0.3 | 12.3663 | 1 | 143 | 94.3597 | 142 | 0.82 | 0.078 | 150.52 | PASS | 141.5396 | 0.95394 | 0.1602 | 3.9275 | 0.94637 | PASS | 0.52678 | 0.36904 | 6.0315 | 1.4534 | PASS | 86.4774 | 100 | 14.3 | PASS | SUITABLE | 3 | MCCB | 94.4 | 100 | Manufacturer-specific adjustable trip unit | 94.4 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 100 A MCCB; target Ir 94.4 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 12.37 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 50 | 0.82 | 22 | 142 | 0.82 | 0.078 | 143
6 | Motor | 250 | 4.5 | 70 | VFD | 35 | 3C / Al / XLPE / Armoured | 19 | 2 | 415 | 0.53 | 0.85 | 0.954 | 0.06 | 1.5 | 0.3 | 7.7289 | 1 | 143 | 120.0942 | 117 | 1.11 | 0.08 | 124.02 | PASS | 180.1413 | 0.95394 | 0.20466 | 3.8314 | 0.92322 | PASS | 0.52678 | 0.49282 | 6.1507 | 1.4821 | PASS | 54.0484 | 70 | 10.01 | PASS | SUITABLE | 3 | MCCB | 120.1 | 125 | Manufacturer-specific adjustable trip unit | 120.1 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 125 A MCCB; target Ir 120.1 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 7.73 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 35 | 1.11 | 19 | 117 | 1.11 | 0.08 | 143
7 | Motor | 400 | 4.5 | 110 | VFD | 240 | 3C / Al / XLPE / Armoured | 43 | 1 | 415 | 0.53 | 0.85 | 0.954 | 0.06 | 1.5 | 0.3 | 12.3663 | 1 | 143 | 188.7194 | 399 | 0.162 | 0.072 | 211.47 | PASS | 283.0792 | 0.95394 | 0.11728 | 3.4503 | 0.8314 | PASS | 0.52678 | 0.17563 | 3.4445 | 0.82999 | PASS | 86.4774 | 240 | 34.32 | PASS | SUITABLE | 3 | MCCB | 188.7 | 200 | Manufacturer-specific adjustable trip unit | 188.7 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 200 A MCCB; target Ir 188.7 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 12.37 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 240 | 0.162 | 43 | 399 | 0.162 | 0.072 | 143
8 | Screen | 250 | 4.5 | 3.7 | DOL | 70 | 4C / Al / XLPE / Armoured | 27.5 | 1 | 415 | 0.53 | 0.76 | 0.88 | 0.06 | 1.5 | 0.3 | 7.7289 | 1 | 143 | 7.6966 | 173 | 0.567 | 0.077 | 91.69 | PASS | 11.5448 | 0.95394 | 0.24355 | 0.29221 | 0.070412 | PASS | 0.64992 | 0.48096 | 0.3847 | 0.092699 | PASS | 54.0484 | 70 | 10.01 | PASS | SUITABLE | 3 | MCCB | 7.7 | 16 | Manufacturer-specific adjustable trip unit | 7.7 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 7.7 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 7.73 kA | PASS | XLPE | 4C | Al | XLPE | Armoured | 70 | 1.05 | 27.5 | 173 | 0.567 | 0.077 | 143
9 | Dissolved Air Generator | 100 | 4.5 | 22 | Star-Delta | 25 | 3C / Al / XLPE / Armoured | 17.5 | 2 | 400 | 0.53 | 0.8 | 0.9 | 0.001 | 1.5 | 0.3 | 3.2075 | 1 | 143 | 44.1031 | 96 | 1.54 | 0.08 | 101.76 | PASS | 66.1547 | 0.95394 | 0.26916 | 0.030841 | 0.0077102 | PASS | 0.6 | 0.64 | 0.048889 | 0.012222 | PASS | 22.4301 | 50 | 7.15 | PASS | SUITABLE | 3 | MCCB | 44.1 | 50 | Manufacturer-specific adjustable trip unit | 44.1 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 50 A MCCB; target Ir 44.1 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 3.21 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 25 | 1.54 | 17.5 | 96 | 1.54 | 0.08 | 143
10 | Air Compressor | 75 | 4.5 | 5.5 | DOL | 25 | 3C / Cu / XLPE / Unarmoured | 16.8 | 1 | 400 | 0.53 | 0.8 | 0.8 | 0.001 | 1.5 | 0.3 | 2.4056 | 0.2 | 143 | 12.404 | 120 | 0.93 | 0.08 | 63.6 | PASS | 18.606 | 0.95394 | 0.35532 | 0.011451 | 0.0028626 | PASS | 0.6 | 0.792 | 0.017016 | 0.0042539 | PASS | 7.5233 | 25 | 7.9939 | PASS | SUITABLE | 3 | MCCB | 12.4 | 16 | Manufacturer-specific adjustable trip unit | 12.4 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 12.4 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 2.41 kA | PASS | XLPE | 3C | Cu | XLPE | Unarmoured | 25 | 1.232 | 16.8 | 120 | 0.93 | 0.08 | 143
11 | DAF Rake Mechanism | 75 | 4.5 | 1.1 | VFD | 25 | 3C / Cu / XLPE / Unarmoured | 16.8 | 1 | 400 | 0.53 | 0.8 | 0.9 | 0.001 | 1.5 | 0.3 | 2.4056 | 0.2 | 143 | 2.2052 | 120 | 0.93 | 0.08 | 63.6 | PASS | 3.3077 | 0.95394 | 0.35532 | 0.0020357 | 0.00050891 | PASS | 0.6 | 0.792 | 0.003025 | 0.00075625 | PASS | 7.5233 | 25 | 7.9939 | PASS | SUITABLE | 3 | MCCB | 2.2 | 16 | Manufacturer-specific adjustable trip unit | 2.2 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 2.2 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 2.41 kA | PASS | XLPE | 3C | Cu | XLPE | Unarmoured | 25 | 1.232 | 16.8 | 120 | 0.93 | 0.08 | 143
12 | Air Dryer | 75 | 4.5 | 0.3 | Direct/Non-Motor | 25 | 3C / Cu / XLPE / Unarmoured | 16.8 | 1 | 230 | 0.53 | 0.8 | 0.8 | 0.001 | 1.5 | 0.3 | 4.1837 | 0.2 | 143 | 2.038 | 120 | 0.93 | 0.08 | 63.6 | PASS | 3.0571 | 0.95394 | 0.35532 | 0.0018814 | 0.000818 | PASS | 0.6 | 0.792 | 0.0027958 | 0.0012155 | PASS | 13.084 | 25 | 7.9939 | PASS | SUITABLE | 3 | MCB | 2 | 16 | Manufacturer-specific adjustable trip unit | 2 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 2.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 4.18 kA | PASS | XLPE | 3C | Cu | XLPE | Unarmoured | 25 | 1.232 | 16.8 | 120 | 0.93 | 0.08 | 143
13 | Auto drain vavle - 01 | 75 | 4.5 | 0.05 | Direct/Non-Motor | 25 | 3C / Al / XLPE / Armoured | 17.5 | 1 | 230 | 0.53 | 0.8 | 0.8 | 0.001 | 1.5 | 0.3 | 4.1837 | 0.2 | 143 | 0.33967 | 96 | 1.54 | 0.08 | 50.88 | PASS | 0.50951 | 0.95394 | 0.53832 | 0.00047506 | 0.00020655 | PASS | 0.6 | 1.28 | 0.00075307 | 0.00032742 | PASS | 13.084 | 25 | 7.9939 | PASS | SUITABLE | 3 | MCB | 0.3 | 16 | Manufacturer-specific adjustable trip unit | 0.3 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.3 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 4.18 kA | PASS | XLPE | 3C | Al | XLPE | Armoured | 25 | 1.54 | 17.5 | 96 | 1.54 | 0.08 | 143
14 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
15 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
16 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
17 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
18 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
19 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
20 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
21 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
22 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
23 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
24 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
25 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
26 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
27 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
28 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
29 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
30 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
31 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
32 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
33 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
34 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
35 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
36 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
37 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
38 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
39 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
41 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
42 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
43 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
44 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
45 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
46 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
47 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
48 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
49 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
50 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
51 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
52 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
53 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
54 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
55 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
56 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
57 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
58 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
59 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
60 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
61 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
62 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
63 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
64 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
65 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
66 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
67 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
68 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
69 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
70 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
71 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
72 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
73 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
74 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
75 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
76 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
77 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
78 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
79 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
80 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
81 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
82 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
83 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
84 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
85 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
86 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
87 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
88 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
89 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
90 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
91 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
92 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
93 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
94 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
95 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
96 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
97 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
98 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
99 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0
100 |  |  | 4.5 |  | VFD |  | 3C / Al / XLPE / Armoured | 0 | 1 | 415 | 0.53 | 0.85 | 0.954 |  | 1.5 | 0.3 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | PASS | 0 | 0.95394 | 0 | 0 | 0 | PASS | 0.52678 | 0 | 0 | 0 | PASS |  |  |  | PASS |  |  |  | 0 | 16 | Manufacturer-specific adjustable trip unit | 0 | Verify manufacturer instantaneous/magnetic pickup | VERIFY MANUFACTURER | PASS | 16 A MCCB; target Ir 0.0 A; manufacturer trip-unit verification required |  | ENTER CB Icu/Ics | Enter manufacturer CB Icu/Ics. Required ≥ 0.00 kA | PASS | XLPE | 3C | Al | XLPE | Armoured |  | 0 | 0 | 0 | 0 | 0 | 0

## Bulk Instructions
OS-DORAEN — VOLUME 3 ¦ AUTOMATIC CABLE SIZING ¦ USER GUIDE
1 | Enter inputs | Enter equipment/tag, transformer kVA, transformer nameplate Z%, motor kW, starting method, cable construction, runs, voltage, derating factor, PF, efficiency, cable length, starting multiplier/PF and fault time. Never type a cable size.
2 | Automatic selection | The hidden AUTO ENGINE evaluates all standard sizes in the Cable Data Master for current capacity, starting VD, running VD and cable short-circuit withstand, then returns the smallest passing size.
3 | Transformer SC | Prospective 3-phase SC current is calculated from transformer kVA, LV voltage and nameplate Z%. The previous hard-coded 4.5% calculation has been removed; sample rows retain 4.5% only as an editable starting value.
4 | Voltage drop | If both R and X are available for the selected cable, VD uses R/X. Otherwise the manufacturer VD reference is used. The method is recorded in AUTO ENGINE.
5 | Short circuit | Cable withstand uses I = k×S/√t. k follows the Volume 3 reference (PVC 115, XLPE 143, EPR 134); verify the applicable cable standard/project basis.
6 | MCCB | The standard MCCB frame is the next listed rating ≥ design current. Long-time setting is a target and must be confirmed as an available manufacturer trip-unit setting. Icu/Ics is a separate manufacturer input.
7 | Final cable result | SUITABLE is based only on cable current capacity, starting VD, running VD and cable SC checks. Missing CB manufacturer data no longer makes the cable result fail.
8 | Data control | Use approved manufacturer/project cable data in Cable Data Master. Reference values must be verified before final engineering issue.

## Motor Calculation
TYPICAL 415V LT POWER CABLE SIZING — LT MOTOR
INPUT DATA — AS PER PROVIDED PDF
Rating of Motor | 45 | kW
Proposed cable size | 25 | mm²
Cable cores | 3C
No. of runs of cable | 2 | runs
Voltage rating | 415 | V
Cable derating factor | 0.53
Allowable running voltage drop | 2.5 | %
Allowable starting voltage drop | 10 | %
Starting power factor (Cos θs) | 0.3
Starting reactive power factor (Sin θs) | 0.95
Running power factor (Cos θr) | 0.85
Running reactive power factor (Sin θr) | 0.53
Motor efficiency | 0.93
Cable resistance R @ 90°C | 0.41 | Ω/km
Cable reactance X @ 50 Hz | 0.0724 | Ω/km
Cable current rating in air | 94 | A | Automatically linked to Cable Data using Proposed cable size.
Maximum cable length | 0.1 | km
Starting-current multiplier | 3 | ×
CALCULATED DATA — PDF METHOD
Full-load current / FLC | 79.1958 | A | Rated kW / (√3 × V × PF × η)
Cable derated current | 99.64 | A | No. of runs × derating factor × cable current rating
Current-carrying capacity check | PASS |  | Derated cable current ≥ FLC
Starting current | 237.5873 | A | Starting current = multiplier × FLC
Starting cable impedance | 0.09589 | Ω | (R Cosθs + X Sinθs) / No. of runs
Starting voltage drop | 3.946 | V | √3 × cable length × starting current × starting impedance
Starting voltage drop % | 0.95084 | % | Starting VD / voltage × 100
Starting VD check | PASS |  | Starting VD % ≤ allowable starting VD
Running cable impedance | 0.19344 | Ω | (R Cosθr + X Sinθr) / No. of runs
Running voltage drop | 2.6534 | V | √3 × cable length × FLC × running impedance
Running voltage drop % | 0.63937 | % | Running VD / voltage × 100
Running VD check | PASS |  | Running VD % ≤ allowable running VD
FINAL CABLE CHECK | SUITABLE |  | All PDF conditions must pass
SHORT-CIRCUIT CHECK
Prospective fault current | 12 | kA
Fault current in A | 12000 | A
Fault clearing time | 0.2 | s
k factor — Aluminium XLPE reference | 94
Minimum S required | 50 | mm² | S = I×√t/k , use this instead S=cable size x No. of Runs
Cable short-circuit withstand | 10.5095 | kA | I_withstand = k×S/√t
SC check | FAIL

## Cable Data
Core | Conductor | Insulation | Armour | Size (mm²) | Cable | OD (mm) | Ampacity Ground (A) | Ampacity Air (A) | Voltage Drop Ref. (V/A/km) | Source / Status | R (Ω/km) | X (Ω/km) | Cable Key | IMPORTANT
3C | Al | XLPE | Armoured | 25 | 3C x 25 Al XLPE Armoured | 17.5 | 94 | 96 | 1.54 | KEI published 3-core Al XLPE reference | 1.54 | 0.08 | 25¦3C / Al / XLPE / Armoured | Enter R and X once in this master sheet for each cable type. Bulk Calculator will automatically use them.
3C | Al | XLPE | Unarmoured | 25 | 3C x 25 Al XLPE Unarmoured | 16.4 | 94 | 96 | 1.54 | KEI published 3-core Al XLPE reference |  |  | 25¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 35 | 3C x 35 Al XLPE Armoured | 19 | 113 | 117 | 1.11 | KEI published 3-core Al XLPE reference |  |  | 35¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 35 | 3C x 35 Al XLPE Unarmoured | 17.9 | 113 | 117 | 1.11 | KEI published 3-core Al XLPE reference |  |  | 35¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 50 | 3C x 50 Al XLPE Armoured | 22 | 133 | 142 | 0.82 | KEI published 3-core Al XLPE reference |  |  | 50¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 50 | 3C x 50 Al XLPE Unarmoured | 20.7 | 133 | 142 | 0.82 | KEI published 3-core Al XLPE reference |  |  | 50¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 70 | 3C x 70 Al XLPE Armoured | 25 | 164 | 179 | 0.567 | KEI published 3-core Al XLPE reference |  |  | 70¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 70 | 3C x 70 Al XLPE Unarmoured | 23.5 | 164 | 179 | 0.567 | KEI published 3-core Al XLPE reference |  |  | 70¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 95 | 3C x 95 Al XLPE Armoured | 28 | 196 | 221 | 0.41 | KEI published 3-core Al XLPE reference |  |  | 95¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 95 | 3C x 95 Al XLPE Unarmoured | 26.3 | 196 | 221 | 0.41 | KEI published 3-core Al XLPE reference |  |  | 95¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 120 | 3C x 120 Al XLPE Armoured | 31 | 223 | 257 | 0.325 | KEI published 3-core Al XLPE reference |  |  | 120¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 120 | 3C x 120 Al XLPE Unarmoured | 29.1 | 223 | 257 | 0.325 | KEI published 3-core Al XLPE reference |  |  | 120¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 150 | 3C x 150 Al XLPE Armoured | 34 | 249 | 292 | 0.265 | KEI published 3-core Al XLPE reference |  |  | 150¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 150 | 3C x 150 Al XLPE Unarmoured | 32 | 249 | 292 | 0.265 | KEI published 3-core Al XLPE reference |  |  | 150¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 185 | 3C x 185 Al XLPE Armoured | 38 | 282 | 337 | 0.211 | KEI published 3-core Al XLPE reference |  |  | 185¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 185 | 3C x 185 Al XLPE Unarmoured | 35.7 | 282 | 337 | 0.211 | KEI published 3-core Al XLPE reference |  |  | 185¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 240 | 3C x 240 Al XLPE Armoured | 43 | 326 | 399 | 0.162 | KEI published 3-core Al XLPE reference |  |  | 240¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 240 | 3C x 240 Al XLPE Unarmoured | 40.4 | 326 | 399 | 0.162 | KEI published 3-core Al XLPE reference |  |  | 240¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 300 | 3C x 300 Al XLPE Armoured | 48 | 367 | 455 | 0.13 | KEI published 3-core Al XLPE reference |  |  | 300¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 300 | 3C x 300 Al XLPE Unarmoured | 45.1 | 367 | 455 | 0.13 | KEI published 3-core Al XLPE reference |  |  | 300¦3C / Al / XLPE / Unarmoured
3C | Al | XLPE | Armoured | 400 | 3C x 400 Al XLPE Armoured | 54 | 418 | 530 | 0.1023 | KEI published 3-core Al XLPE reference |  |  | 400¦3C / Al / XLPE / Armoured
3C | Al | XLPE | Unarmoured | 400 | 3C x 400 Al XLPE Unarmoured | 50.8 | 418 | 530 | 0.1023 | KEI published 3-core Al XLPE reference |  |  | 400¦3C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 16 | 3.5C x 16 Al XLPE Armoured | 15.9 | 73 | 73 | 4.24 | Reference table from previous workbook |  |  | 16¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 16 | 3.5C x 16 Al XLPE Unarmoured | 14.9 | 73 | 73 | 4.24 | Reference table from previous workbook |  |  | 16¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 25 | 3.5C x 25 Al XLPE Armoured | 18.6 | 95 | 95 | 2.67 | Reference table from previous workbook |  |  | 25¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 25 | 3.5C x 25 Al XLPE Unarmoured | 17.4 | 95 | 95 | 2.67 | Reference table from previous workbook |  |  | 25¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 35 | 3.5C x 35 Al XLPE Armoured | 20.1 | 114 | 114 | 1.94 | Reference table from previous workbook |  |  | 35¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 35 | 3.5C x 35 Al XLPE Unarmoured | 18.9 | 114 | 114 | 1.94 | Reference table from previous workbook |  |  | 35¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 50 | 3.5C x 50 Al XLPE Armoured | 23.3 | 134 | 138 | 1.44 | Reference table from previous workbook |  |  | 50¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 50 | 3.5C x 50 Al XLPE Unarmoured | 21.9 | 134 | 138 | 1.44 | Reference table from previous workbook |  |  | 50¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 70 | 3.5C x 70 Al XLPE Armoured | 26.5 | 164 | 175 | 1 | Reference table from previous workbook |  |  | 70¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 70 | 3.5C x 70 Al XLPE Unarmoured | 24.9 | 164 | 175 | 1 | Reference table from previous workbook |  |  | 70¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 95 | 3.5C x 95 Al XLPE Armoured | 29.7 | 197 | 216 | 0.7 | Reference table from previous workbook |  |  | 95¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 95 | 3.5C x 95 Al XLPE Unarmoured | 27.9 | 197 | 216 | 0.7 | Reference table from previous workbook |  |  | 95¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 120 | 3.5C x 120 Al XLPE Armoured | 32.9 | 223 | 249 | 0.56 | Reference table from previous workbook |  |  | 120¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 120 | 3.5C x 120 Al XLPE Unarmoured | 30.9 | 223 | 249 | 0.56 | Reference table from previous workbook |  |  | 120¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 150 | 3.5C x 150 Al XLPE Armoured | 36 | 249 | 284 | 0.48 | Reference table from previous workbook |  |  | 150¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 150 | 3.5C x 150 Al XLPE Unarmoured | 33.9 | 249 | 284 | 0.48 | Reference table from previous workbook |  |  | 150¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 185 | 3.5C x 185 Al XLPE Armoured | 40.3 | 282 | 329 | 0.4 | Reference table from previous workbook |  |  | 185¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 185 | 3.5C x 185 Al XLPE Unarmoured | 37.9 | 282 | 329 | 0.4 | Reference table from previous workbook |  |  | 185¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 240 | 3.5C x 240 Al XLPE Armoured | 45.6 | 327 | 392 | 0.3 | Reference table from previous workbook |  |  | 240¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 240 | 3.5C x 240 Al XLPE Unarmoured | 42.8 | 327 | 392 | 0.3 | Reference table from previous workbook |  |  | 240¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 300 | 3.5C x 300 Al XLPE Armoured | 50.9 | 369 | 452 | 0.26 | Reference table from previous workbook |  |  | 300¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 300 | 3.5C x 300 Al XLPE Unarmoured | 47.8 | 369 | 452 | 0.26 | Reference table from previous workbook |  |  | 300¦3.5C / Al / XLPE / Unarmoured
3.5C | Al | XLPE | Armoured | 400 | 3.5C x 400 Al XLPE Armoured | 57.2 | 420 | 526 | 0.21 | Reference table from previous workbook |  |  | 400¦3.5C / Al / XLPE / Armoured
3.5C | Al | XLPE | Unarmoured | 400 | 3.5C x 400 Al XLPE Unarmoured | 53.8 | 420 | 526 | 0.21 | Reference table from previous workbook |  |  | 400¦3.5C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 16 | 4C x 16 Al XLPE Armoured | 16.5 | 70 | 73 | 4.5 | Project-reference; verify manufacturer |  |  | 16¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 16 | 4C x 16 Al XLPE Unarmoured | 15.5 | 70 | 73 | 4.5 | Project-reference; verify manufacturer |  |  | 16¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 25 | 4C x 25 Al XLPE Armoured | 19.2 | 92 | 95 | 2.8 | Project-reference; verify manufacturer |  |  | 25¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 25 | 4C x 25 Al XLPE Unarmoured | 18.1 | 92 | 95 | 2.8 | Project-reference; verify manufacturer | 1.54 | 0.08 | 25¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 35 | 4C x 35 Al XLPE Armoured | 20.9 | 110 | 115 | 2 | Project-reference; verify manufacturer |  |  | 35¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 35 | 4C x 35 Al XLPE Unarmoured | 19.6 | 110 | 115 | 2 | Project-reference; verify manufacturer |  |  | 35¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 50 | 4C x 50 Al XLPE Armoured | 24.2 | 130 | 137 | 1.5 | Project-reference; verify manufacturer |  |  | 50¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 50 | 4C x 50 Al XLPE Unarmoured | 22.7 | 130 | 137 | 1.5 | Project-reference; verify manufacturer |  |  | 50¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 70 | 4C x 70 Al XLPE Armoured | 27.5 | 160 | 173 | 1.05 | Project-reference; verify manufacturer |  |  | 70¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 70 | 4C x 70 Al XLPE Unarmoured | 25.9 | 160 | 173 | 1.05 | Project-reference; verify manufacturer |  |  | 70¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 95 | 4C x 95 Al XLPE Armoured | 30.8 | 192 | 214 | 0.72 | Project-reference; verify manufacturer |  |  | 95¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 95 | 4C x 95 Al XLPE Unarmoured | 29 | 192 | 214 | 0.72 | Project-reference; verify manufacturer |  |  | 95¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 120 | 4C x 120 Al XLPE Armoured | 34.1 | 218 | 247 | 0.57 | Project-reference; verify manufacturer |  |  | 120¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 120 | 4C x 120 Al XLPE Unarmoured | 32.1 | 218 | 247 | 0.57 | Project-reference; verify manufacturer |  |  | 120¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 150 | 4C x 150 Al XLPE Armoured | 37.4 | 245 | 280 | 0.49 | Project-reference; verify manufacturer |  |  | 150¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 150 | 4C x 150 Al XLPE Unarmoured | 35.2 | 245 | 280 | 0.49 | Project-reference; verify manufacturer |  |  | 150¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 185 | 4C x 185 Al XLPE Armoured | 41.8 | 278 | 325 | 0.41 | Project-reference; verify manufacturer |  |  | 185¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 185 | 4C x 185 Al XLPE Unarmoured | 39.3 | 278 | 325 | 0.41 | Project-reference; verify manufacturer |  |  | 185¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 240 | 4C x 240 Al XLPE Armoured | 47.3 | 322 | 388 | 0.31 | Project-reference; verify manufacturer |  |  | 240¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 240 | 4C x 240 Al XLPE Unarmoured | 44.5 | 322 | 388 | 0.31 | Project-reference; verify manufacturer |  |  | 240¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 300 | 4C x 300 Al XLPE Armoured | 52.8 | 363 | 447 | 0.27 | Project-reference; verify manufacturer |  |  | 300¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 300 | 4C x 300 Al XLPE Unarmoured | 49.6 | 363 | 447 | 0.27 | Project-reference; verify manufacturer |  |  | 300¦4C / Al / XLPE / Unarmoured
4C | Al | XLPE | Armoured | 400 | 4C x 400 Al XLPE Armoured | 59.4 | 412 | 520 | 0.22 | Project-reference; verify manufacturer |  |  | 400¦4C / Al / XLPE / Armoured
4C | Al | XLPE | Unarmoured | 400 | 4C x 400 Al XLPE Unarmoured | 55.8 | 412 | 520 | 0.22 | Project-reference; verify manufacturer |  |  | 400¦4C / Al / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 25 | 3C x 25 Cu XLPE Armoured (approx.) | 17.9 | 117.5 | 120 | 1.232 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 25 | 3C x 25 Cu XLPE Unarmoured (approx.) | 16.8 | 117.5 | 120 | 1.232 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 35 | 3C x 35 Cu XLPE Armoured (approx.) | 19.4 | 141.2 | 146.2 | 0.888 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 35 | 3C x 35 Cu XLPE Unarmoured (approx.) | 18.2 | 141.2 | 146.2 | 0.888 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 50 | 3C x 50 Cu XLPE Armoured (approx.) | 22.4 | 166.2 | 177.5 | 0.656 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 50 | 3C x 50 Cu XLPE Unarmoured (approx.) | 21.1 | 166.2 | 177.5 | 0.656 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 70 | 3C x 70 Cu XLPE Armoured (approx.) | 25.5 | 205 | 223.8 | 0.454 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 70 | 3C x 70 Cu XLPE Unarmoured (approx.) | 24 | 205 | 223.8 | 0.454 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 95 | 3C x 95 Cu XLPE Armoured (approx.) | 28.6 | 245 | 276.2 | 0.328 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 95 | 3C x 95 Cu XLPE Unarmoured (approx.) | 26.8 | 245 | 276.2 | 0.328 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 120 | 3C x 120 Cu XLPE Armoured (approx.) | 31.6 | 278.8 | 321.2 | 0.26 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 120 | 3C x 120 Cu XLPE Unarmoured (approx.) | 29.7 | 278.8 | 321.2 | 0.26 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 150 | 3C x 150 Cu XLPE Armoured (approx.) | 34.7 | 311.2 | 365 | 0.212 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 150 | 3C x 150 Cu XLPE Unarmoured (approx.) | 32.6 | 311.2 | 365 | 0.212 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 185 | 3C x 185 Cu XLPE Armoured (approx.) | 38.8 | 352.5 | 421.2 | 0.169 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 185 | 3C x 185 Cu XLPE Unarmoured (approx.) | 36.4 | 352.5 | 421.2 | 0.169 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 240 | 3C x 240 Cu XLPE Armoured (approx.) | 43.9 | 407.5 | 498.8 | 0.13 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 240 | 3C x 240 Cu XLPE Unarmoured (approx.) | 41.2 | 407.5 | 498.8 | 0.13 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 300 | 3C x 300 Cu XLPE Armoured (approx.) | 49 | 458.8 | 568.8 | 0.104 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 300 | 3C x 300 Cu XLPE Unarmoured (approx.) | 46 | 458.8 | 568.8 | 0.104 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦3C / Cu / XLPE / Unarmoured
3C | Cu | XLPE | Armoured | 400 | 3C x 400 Cu XLPE Armoured (approx.) | 55.1 | 522.5 | 662.5 | 0.082 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦3C / Cu / XLPE / Armoured
3C | Cu | XLPE | Unarmoured | 400 | 3C x 400 Cu XLPE Unarmoured (approx.) | 51.8 | 522.5 | 662.5 | 0.082 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦3C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 16 | 3.5C x 16 Cu XLPE Armoured (approx.) | 16.2 | 91.2 | 91.2 | 3.392 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 16¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 16 | 3.5C x 16 Cu XLPE Unarmoured (approx.) | 15.2 | 91.2 | 91.2 | 3.392 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 16¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 25 | 3.5C x 25 Cu XLPE Armoured (approx.) | 18.9 | 118.8 | 118.8 | 2.136 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 25 | 3.5C x 25 Cu XLPE Unarmoured (approx.) | 17.8 | 118.8 | 118.8 | 2.136 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 35 | 3.5C x 35 Cu XLPE Armoured (approx.) | 20.5 | 142.5 | 142.5 | 1.552 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 35 | 3.5C x 35 Cu XLPE Unarmoured (approx.) | 19.3 | 142.5 | 142.5 | 1.552 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 50 | 3.5C x 50 Cu XLPE Armoured (approx.) | 23.8 | 167.5 | 172.5 | 1.152 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 50 | 3.5C x 50 Cu XLPE Unarmoured (approx.) | 22.4 | 167.5 | 172.5 | 1.152 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 70 | 3.5C x 70 Cu XLPE Armoured (approx.) | 27 | 205 | 218.8 | 0.8 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 70 | 3.5C x 70 Cu XLPE Unarmoured (approx.) | 25.4 | 205 | 218.8 | 0.8 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 95 | 3.5C x 95 Cu XLPE Armoured (approx.) | 30.3 | 246.2 | 270 | 0.56 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 95 | 3.5C x 95 Cu XLPE Unarmoured (approx.) | 28.5 | 246.2 | 270 | 0.56 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 120 | 3.5C x 120 Cu XLPE Armoured (approx.) | 33.5 | 278.8 | 311.2 | 0.448 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 120 | 3.5C x 120 Cu XLPE Unarmoured (approx.) | 31.5 | 278.8 | 311.2 | 0.448 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 150 | 3.5C x 150 Cu XLPE Armoured (approx.) | 36.8 | 311.2 | 355 | 0.384 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 150 | 3.5C x 150 Cu XLPE Unarmoured (approx.) | 34.6 | 311.2 | 355 | 0.384 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 185 | 3.5C x 185 Cu XLPE Armoured (approx.) | 41.1 | 352.5 | 411.2 | 0.32 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 185 | 3.5C x 185 Cu XLPE Unarmoured (approx.) | 38.6 | 352.5 | 411.2 | 0.32 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 240 | 3.5C x 240 Cu XLPE Armoured (approx.) | 46.5 | 408.8 | 490 | 0.24 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 240 | 3.5C x 240 Cu XLPE Unarmoured (approx.) | 43.7 | 408.8 | 490 | 0.24 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 300 | 3.5C x 300 Cu XLPE Armoured (approx.) | 51.9 | 461.2 | 565 | 0.208 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 300 | 3.5C x 300 Cu XLPE Unarmoured (approx.) | 48.8 | 461.2 | 565 | 0.208 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦3.5C / Cu / XLPE / Unarmoured
3.5C | Cu | XLPE | Armoured | 400 | 3.5C x 400 Cu XLPE Armoured (approx.) | 58.4 | 525 | 657.5 | 0.168 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦3.5C / Cu / XLPE / Armoured
3.5C | Cu | XLPE | Unarmoured | 400 | 3.5C x 400 Cu XLPE Unarmoured (approx.) | 54.9 | 525 | 657.5 | 0.168 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦3.5C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 16 | 4C x 16 Cu XLPE Armoured (approx.) | 16.8 | 87.5 | 91.2 | 3.6 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 16¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 16 | 4C x 16 Cu XLPE Unarmoured (approx.) | 15.8 | 87.5 | 91.2 | 3.6 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 16¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 25 | 4C x 25 Cu XLPE Armoured (approx.) | 19.6 | 115 | 118.8 | 2.24 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 25 | 4C x 25 Cu XLPE Unarmoured (approx.) | 18.5 | 115 | 118.8 | 2.24 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 25¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 35 | 4C x 35 Cu XLPE Armoured (approx.) | 21.3 | 137.5 | 143.8 | 1.6 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 35 | 4C x 35 Cu XLPE Unarmoured (approx.) | 20 | 137.5 | 143.8 | 1.6 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 35¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 50 | 4C x 50 Cu XLPE Armoured (approx.) | 24.7 | 162.5 | 171.2 | 1.2 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 50 | 4C x 50 Cu XLPE Unarmoured (approx.) | 23.2 | 162.5 | 171.2 | 1.2 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 50¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 70 | 4C x 70 Cu XLPE Armoured (approx.) | 28.1 | 200 | 216.2 | 0.84 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 70 | 4C x 70 Cu XLPE Unarmoured (approx.) | 26.4 | 200 | 216.2 | 0.84 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 70¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 95 | 4C x 95 Cu XLPE Armoured (approx.) | 31.4 | 240 | 267.5 | 0.576 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 95 | 4C x 95 Cu XLPE Unarmoured (approx.) | 29.5 | 240 | 267.5 | 0.576 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 95¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 120 | 4C x 120 Cu XLPE Armoured (approx.) | 34.8 | 272.5 | 308.8 | 0.456 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 120 | 4C x 120 Cu XLPE Unarmoured (approx.) | 32.7 | 272.5 | 308.8 | 0.456 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 120¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 150 | 4C x 150 Cu XLPE Armoured (approx.) | 38.1 | 306.2 | 350 | 0.392 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 150 | 4C x 150 Cu XLPE Unarmoured (approx.) | 35.9 | 306.2 | 350 | 0.392 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 150¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 185 | 4C x 185 Cu XLPE Armoured (approx.) | 42.6 | 347.5 | 406.2 | 0.328 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 185 | 4C x 185 Cu XLPE Unarmoured (approx.) | 40.1 | 347.5 | 406.2 | 0.328 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 185¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 240 | 4C x 240 Cu XLPE Armoured (approx.) | 48.2 | 402.5 | 485 | 0.248 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 240 | 4C x 240 Cu XLPE Unarmoured (approx.) | 45.4 | 402.5 | 485 | 0.248 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 240¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 300 | 4C x 300 Cu XLPE Armoured (approx.) | 53.9 | 453.8 | 558.8 | 0.216 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 300 | 4C x 300 Cu XLPE Unarmoured (approx.) | 50.6 | 453.8 | 558.8 | 0.216 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 300¦4C / Cu / XLPE / Unarmoured
4C | Cu | XLPE | Armoured | 400 | 4C x 400 Cu XLPE Armoured (approx.) | 60.6 | 515 | 650 | 0.176 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦4C / Cu / XLPE / Armoured
4C | Cu | XLPE | Unarmoured | 400 | 4C x 400 Cu XLPE Unarmoured (approx.) | 57 | 515 | 650 | 0.176 | Approx. Cu reference (25% current-rating uplift); verify manufacturer |  |  | 400¦4C / Cu / XLPE / Unarmoured

## Formula Guide
OS-DORAEN VOLUME 3 — FORMULA & LOGIC GUIDE
1. FLC | I = P×1000 / (√3×V×PF×η) | Motor full-load current.
2. Derated capacity | I_z = Runs × Derating Factor × Cable Ampacity | Continuous current check.
3. Starting current | I_start = Starting Multiplier × FLC | Starting multiplier is a design input.
4. Starting VD | R/X method when R and X are available; otherwise VD reference | Compared with OS-DORAEN B6.
5. Running VD | R/X method when R and X are available; otherwise VD reference | Compared with OS-DORAEN B5.
6. Transformer SC | I_sc = S×1000 / [√3×V×(Z%/100)] | Prospective 3-phase fault current at LV terminals.
7. Cable SC | I_cable = k×S/√t | S = total area of parallel runs.
8. Auto selection | Smallest standard cable with all four cable checks PASS | No manual cable-size entry.
9. MCCB frame | Next standard rating ≥ design current | Uses Lists!J standard rating table.
10. Cable coordination | I_b ≤ I_r,target ≤ I_z | Actual trip-unit setting availability must be verified.
11. CB short-circuit | Icu/Ics ≥ prospective SC | Icu/Ics is manufacturer/project input.

## Design Notes
OS-DORAEN — DESIGN & RELEASE NOTES
Engineering basis
Volume 3 workflow: FLC → starting current → derating → current capacity → starting VD → running VD → short-circuit withstand → final cable selection.
Transformer SC
Prospective SC is calculated from transformer kVA, LV voltage and transformer nameplate Z%. Existing sample rows retain 4.5% as an editable starting input only.
Protection coordination
MCCB frame is selected from the standard list. Long-time setting is a target; actual trip-unit setting and instantaneous/magnetic characteristics require manufacturer verification. Icu/Ics is a separate input.
Data integrity
Cable ampacity, R, X, VD reference, OD and kSC come from Cable Data Master. Verify approved manufacturer/project data before final issue.
Product status
OS-DORAEN Volume 3 — Automatic Cable Sizing & Protection Review ¦ Release Candidate V1.0

## Lists (hidden)
Cable Construction | Core | Conductor | Insulation | Armour | Cable Size | MCCB Standard Rating (A) | Standard MCCB Rating (A)
3C / Al / XLPE / Armoured | 3C | Al | XLPE | Armoured | 16 | 63 | 16
3C / Al / XLPE / Unarmoured | 3C | Al | XLPE | Unarmoured | 25 | 80 | 20
3.5C / Al / XLPE / Armoured | 3.5C | Al | XLPE | Armoured | 35 | 100 | 25
3.5C / Al / XLPE / Unarmoured | 3.5C | Al | XLPE | Unarmoured | 50 | 125 | 32
4C / Al / XLPE / Armoured | 4C | Al | XLPE | Armoured | 70 | 160 | 40
4C / Al / XLPE / Unarmoured | 4C | Al | XLPE | Unarmoured | 95 | 200 | 50
3C / Cu / XLPE / Armoured | 3C | Cu | XLPE | Armoured | 120 | 250 | 63
3C / Cu / XLPE / Unarmoured | 3C | Cu | XLPE | Unarmoured | 150 | 320 | 80
3.5C / Cu / XLPE / Armoured | 3.5C | Cu | XLPE | Armoured | 185 | 400 | 100
3.5C / Cu / XLPE / Unarmoured | 3.5C | Cu | XLPE | Unarmoured | 240 | 500 | 125
4C / Cu / XLPE / Armoured | 4C | Cu | XLPE | Armoured | 300 | 630 | 160
4C / Cu / XLPE / Unarmoured | 4C | Cu | XLPE | Unarmoured | 400 | 800 | 200
[6 empty] | 1000 | 250
[6 empty] | 1250 | 320
[6 empty] | 1600 | 400
[6 empty] | 2000 | 500
[6 empty] | 2500 | 630
[6 empty] | 3200 | 800
1000
1250
1600
2000
2500
3200
4000
5000
6300

## Cable Data Master
Type | Cores | Material | Insulation | Armour | Size_mm2 | Ampacity_A | R_ohm_km | X_ohm_km | k_SC per Volume 3 reference: PVC 115 ¦ XLPE 143 ¦ EPR 134. Verify applicable standard/project/manufacturer basis. | VD Ref (V/A/km) | OD (mm) | Source / Status | AUTOMATION NOTE | CableInsulationList | CableArmourList | CableSizeList
XLPE | 3C | Al | XLPE | Armoured | 25 | 96 | 1.54 | 0.08 | 143 | 1.54 | 17.5 |  | Columns K:M are synchronized references used by OS-DORAEN/Bulk Calculator. Verify approved manufacturer/project data before final design use.
XLPE | 3C | Al | XLPE | Unarmoured | 25 | 96 | 1.54 | 0.08 | 143 | 1.54 | 16.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 35 | 117 | 1.11 | 0.08 | 143 | 1.11 | 19 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 35 | 117 | 1.11 | 0.08 | 143 | 1.11 | 17.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 50 | 142 | 0.82 | 0.078 | 143 | 0.82 | 22 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 50 | 142 | 0.82 | 0.078 | 143 | 0.82 | 20.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 70 | 179 | 0.567 | 0.077 | 143 | 0.567 | 25 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 70 | 179 | 0.567 | 0.077 | 143 | 0.567 | 23.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 95 | 221 | 0.41 | 0.074 | 143 | 0.41 | 28 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 95 | 221 | 0.41 | 0.074 | 143 | 0.41 | 26.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 120 | 257 | 0.325 | 0.072 | 143 | 0.325 | 31 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 120 | 257 | 0.325 | 0.072 | 143 | 0.325 | 29.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 150 | 292 | 0.265 | 0.072 | 143 | 0.265 | 34 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 150 | 292 | 0.265 | 0.072 | 143 | 0.265 | 32 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 185 | 337 | 0.211 | 0.072 | 143 | 0.211 | 38 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 185 | 337 | 0.211 | 0.072 | 143 | 0.211 | 35.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 240 | 399 | 0.162 | 0.072 | 143 | 0.162 | 43 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 240 | 399 | 0.162 | 0.072 | 143 | 0.162 | 40.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 300 | 455 | 0.13 | 0.071 | 143 | 0.13 | 48 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 300 | 455 | 0.13 | 0.071 | 143 | 0.13 | 45.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Armoured | 400 | 530 | 0.1023 | 0.07 | 143 | 0.1023 | 54 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Al | XLPE | Unarmoured | 400 | 530 | 0.1023 | 0.07 | 143 | 0.1023 | 50.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 16 | 73 | 1.54 | 0.08 | 143 | 4.24 | 15.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 16 | 73 | 1.54 | 0.08 | 143 | 4.24 | 14.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 25 | 95 | 1.54 | 0.08 | 143 | 2.67 | 18.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 25 | 95 | 1.54 | 0.08 | 143 | 2.67 | 17.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 35 | 114 | 1.11 | 0.08 | 143 | 1.94 | 20.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 35 | 114 | 1.11 | 0.08 | 143 | 1.94 | 18.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 50 | 138 | 0.82 | 0.078 | 143 | 1.44 | 23.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 50 | 138 | 0.82 | 0.078 | 143 | 1.44 | 21.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 70 | 175 | 0.567 | 0.077 | 143 | 1 | 26.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 70 | 175 | 0.567 | 0.077 | 143 | 1 | 24.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 95 | 216 | 0.41 | 0.074 | 143 | 0.7 | 29.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 95 | 216 | 0.41 | 0.074 | 143 | 0.7 | 27.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 120 | 249 | 0.325 | 0.072 | 143 | 0.56 | 32.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 120 | 249 | 0.325 | 0.072 | 143 | 0.56 | 30.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 150 | 284 | 0.265 | 0.072 | 143 | 0.48 | 36 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 150 | 284 | 0.265 | 0.072 | 143 | 0.48 | 33.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 185 | 329 | 0.211 | 0.072 | 143 | 0.4 | 40.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 185 | 329 | 0.211 | 0.072 | 143 | 0.4 | 37.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 240 | 392 | 0.162 | 0.072 | 143 | 0.3 | 45.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 240 | 392 | 0.162 | 0.072 | 143 | 0.3 | 42.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 300 | 452 | 0.13 | 0.071 | 143 | 0.26 | 50.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 300 | 452 | 0.13 | 0.071 | 143 | 0.26 | 47.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Armoured | 400 | 526 | 0.1023 | 0.07 | 143 | 0.21 | 57.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Al | XLPE | Unarmoured | 400 | 526 | 0.1023 | 0.07 | 143 | 0.21 | 53.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 16 | 73 | 1.54 | 0.08 | 143 | 4.5 | 16.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 16 | 73 | 1.54 | 0.08 | 143 | 4.5 | 15.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 25 | 95 | 1.54 | 0.08 | 143 | 2.8 | 19.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 25 | 95 | 1.54 | 0.08 | 143 | 2.8 | 18.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 35 | 115 | 1.11 | 0.08 | 143 | 2 | 20.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 35 | 115 | 1.11 | 0.08 | 143 | 2 | 19.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 50 | 137 | 0.82 | 0.078 | 143 | 1.5 | 24.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 50 | 137 | 0.82 | 0.078 | 143 | 1.5 | 22.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 70 | 173 | 0.567 | 0.077 | 143 | 1.05 | 27.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 70 | 173 | 0.567 | 0.077 | 143 | 1.05 | 25.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 95 | 214 | 0.41 | 0.074 | 143 | 0.72 | 30.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 95 | 214 | 0.41 | 0.074 | 143 | 0.72 | 29 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 120 | 247 | 0.325 | 0.072 | 143 | 0.57 | 34.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 120 | 247 | 0.325 | 0.072 | 143 | 0.57 | 32.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 150 | 280 | 0.265 | 0.072 | 143 | 0.49 | 37.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 150 | 280 | 0.265 | 0.072 | 143 | 0.49 | 35.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 185 | 325 | 0.211 | 0.072 | 143 | 0.41 | 41.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 185 | 325 | 0.211 | 0.072 | 143 | 0.41 | 39.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 240 | 388 | 0.162 | 0.072 | 143 | 0.31 | 47.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 240 | 388 | 0.162 | 0.072 | 143 | 0.31 | 44.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 300 | 447 | 0.13 | 0.071 | 143 | 0.27 | 52.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 300 | 447 | 0.13 | 0.071 | 143 | 0.27 | 49.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Armoured | 400 | 520 | 0.1023 | 0.07 | 143 | 0.22 | 59.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Al | XLPE | Unarmoured | 400 | 520 | 0.1023 | 0.07 | 143 | 0.22 | 55.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 25 | 120 | 0.93 | 0.08 | 143 | 1.232 | 17.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 25 | 120 | 0.93 | 0.08 | 143 | 1.232 | 16.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 35 | 146.2 | 0.671 | 0.08 | 143 | 0.888 | 19.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 35 | 146.2 | 0.671 | 0.08 | 143 | 0.888 | 18.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 50 | 177.5 | 0.495 | 0.078 | 143 | 0.656 | 22.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 50 | 177.5 | 0.495 | 0.078 | 143 | 0.656 | 21.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 70 | 223.8 | 0.343 | 0.077 | 143 | 0.454 | 25.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 70 | 223.8 | 0.343 | 0.077 | 143 | 0.454 | 24 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 95 | 276.2 | 0.247 | 0.074 | 143 | 0.328 | 28.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 95 | 276.2 | 0.247 | 0.074 | 143 | 0.328 | 26.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 120 | 321.2 | 0.196 | 0.072 | 143 | 0.26 | 31.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 120 | 321.2 | 0.196 | 0.072 | 143 | 0.26 | 29.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 150 | 365 | 0.159 | 0.072 | 143 | 0.212 | 34.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 150 | 365 | 0.159 | 0.072 | 143 | 0.212 | 32.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 185 | 421.2 | 0.127 | 0.072 | 143 | 0.169 | 38.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 185 | 421.2 | 0.127 | 0.072 | 143 | 0.169 | 36.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 240 | 498.8 | 0.0965 | 0.072 | 143 | 0.13 | 43.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 240 | 498.8 | 0.0965 | 0.072 | 143 | 0.13 | 41.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 300 | 568.8 | 0.0769 | 0.071 | 143 | 0.104 | 49 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 300 | 568.8 | 0.0769 | 0.071 | 143 | 0.104 | 46 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Armoured | 400 | 662.5 | 0.0602 | 0.07 | 143 | 0.082 | 55.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3C | Cu | XLPE | Unarmoured | 400 | 662.5 | 0.0602 | 0.07 | 143 | 0.082 | 51.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 16 | 91.2 | 1.47 | 0.08 | 143 | 3.392 | 16.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 16 | 91.2 | 1.47 | 0.08 | 143 | 3.392 | 15.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 25 | 118.8 | 0.93 | 0.08 | 143 | 2.136 | 18.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 25 | 118.8 | 0.93 | 0.08 | 143 | 2.136 | 17.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 35 | 142.5 | 0.671 | 0.08 | 143 | 1.552 | 20.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 35 | 142.5 | 0.671 | 0.08 | 143 | 1.552 | 19.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 50 | 172.5 | 0.495 | 0.078 | 143 | 1.152 | 23.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 50 | 172.5 | 0.495 | 0.078 | 143 | 1.152 | 22.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 70 | 218.8 | 0.343 | 0.077 | 143 | 0.8 | 27 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 70 | 218.8 | 0.343 | 0.077 | 143 | 0.8 | 25.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 95 | 270 | 0.247 | 0.074 | 143 | 0.56 | 30.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 95 | 270 | 0.247 | 0.074 | 143 | 0.56 | 28.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 120 | 311.2 | 0.196 | 0.072 | 143 | 0.448 | 33.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 120 | 311.2 | 0.196 | 0.072 | 143 | 0.448 | 31.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 150 | 355 | 0.159 | 0.072 | 143 | 0.384 | 36.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 150 | 355 | 0.159 | 0.072 | 143 | 0.384 | 34.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 185 | 411.2 | 0.127 | 0.072 | 143 | 0.32 | 41.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 185 | 411.2 | 0.127 | 0.072 | 143 | 0.32 | 38.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 240 | 490 | 0.0965 | 0.072 | 143 | 0.24 | 46.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 240 | 490 | 0.0965 | 0.072 | 143 | 0.24 | 43.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 300 | 565 | 0.0769 | 0.071 | 143 | 0.208 | 51.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 300 | 565 | 0.0769 | 0.071 | 143 | 0.208 | 48.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Armoured | 400 | 657.5 | 0.0602 | 0.07 | 143 | 0.168 | 58.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 3.5C | Cu | XLPE | Unarmoured | 400 | 657.5 | 0.0602 | 0.07 | 143 | 0.168 | 54.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 16 | 91.2 | 1.47 | 0.08 | 143 | 3.6 | 16.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 16 | 91.2 | 1.47 | 0.08 | 143 | 3.6 | 15.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 25 | 118.8 | 0.93 | 0.08 | 143 | 2.24 | 19.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 25 | 118.8 | 0.93 | 0.08 | 143 | 2.24 | 18.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 35 | 143.8 | 0.671 | 0.08 | 143 | 1.6 | 21.3 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 35 | 143.8 | 0.671 | 0.08 | 143 | 1.6 | 20 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 50 | 171.2 | 0.495 | 0.078 | 143 | 1.2 | 24.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 50 | 171.2 | 0.495 | 0.078 | 143 | 1.2 | 23.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 70 | 216.2 | 0.343 | 0.077 | 143 | 0.84 | 28.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 70 | 216.2 | 0.343 | 0.077 | 143 | 0.84 | 26.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 95 | 267.5 | 0.247 | 0.074 | 143 | 0.576 | 31.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 95 | 267.5 | 0.247 | 0.074 | 143 | 0.576 | 29.5 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 120 | 308.8 | 0.196 | 0.072 | 143 | 0.456 | 34.8 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 120 | 308.8 | 0.196 | 0.072 | 143 | 0.456 | 32.7 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 150 | 350 | 0.159 | 0.072 | 143 | 0.392 | 38.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 150 | 350 | 0.159 | 0.072 | 143 | 0.392 | 35.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 185 | 406.2 | 0.127 | 0.072 | 143 | 0.328 | 42.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 185 | 406.2 | 0.127 | 0.072 | 143 | 0.328 | 40.1 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 240 | 485 | 0.0965 | 0.072 | 143 | 0.248 | 48.2 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 240 | 485 | 0.0965 | 0.072 | 143 | 0.248 | 45.4 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 300 | 558.8 | 0.0769 | 0.071 | 143 | 0.216 | 53.9 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 300 | 558.8 | 0.0769 | 0.071 | 143 | 0.216 | 50.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Armoured | 400 | 650 | 0.0602 | 0.07 | 143 | 0.176 | 60.6 |  | Verify approved manufacturer/project data before final issue.
XLPE | 4C | Cu | XLPE | Unarmoured | 400 | 650 | 0.0602 | 0.07 | 143 | 0.176 | 57 |  | Verify approved manufacturer/project data before final issue.

## AUTO ENGINE (hidden)
Bulk Row | Candidate Size mm² | Ampacity A | VD Ref V/A/km | R Ω/km | X Ω/km | k_SC | Current Pass | Starting VD % | Running VD % | SC Withstand kA | SC Pass | ALL CHECKS PASS | VD Method
4 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.47108 | 0.399 | 114.4 | 1 | 1 | R/X
4 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.51585 | 0.47656 | 85.8 | 1 | 1 | R/X
4 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.56686 | 0.56591 | 68.64 | 1 | 1 | R/X
4 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.63791 | 0.70011 | 52.91 | 1 | 1 | R/X
4 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.71621 | 0.84801 | 42.9 | 1 | 1 | R/X
4 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.80321 | 1.0123 | 34.32 | 1 | 1 | R/X
4 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 0 | 0.93568 | 1.2485 | 27.17 | 1 | 0 | R/X
4 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 0 | 1.1772 | 1.6836 | 20.02 | 1 | 0 | R/X
4 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 0 | 1.5486 | 2.3783 | 14.3 | 1 | 0 | R/X
4 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 0 | 1.9783 | 3.1759 | 10.01 | 0 | 0 | R/X
4 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 0 | 2.6018 | 4.3536 | 7.15 | 0 | 0 | R/X
4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
5 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.034546 | 0.02926 | 114.4 | 1 | 1 | R/X
5 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.037829 | 0.034948 | 85.8 | 1 | 1 | R/X
5 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.04157 | 0.0415 | 68.64 | 1 | 1 | R/X
5 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.04678 | 0.051341 | 52.91 | 1 | 1 | R/X
5 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.052522 | 0.062187 | 42.9 | 1 | 1 | R/X
5 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.058902 | 0.074238 | 34.32 | 1 | 1 | R/X
5 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.068616 | 0.091559 | 27.17 | 1 | 1 | R/X
5 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.086325 | 0.12347 | 20.02 | 1 | 1 | R/X
5 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.11356 | 0.17441 | 14.3 | 1 | 1 | R/X
5 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0.14508 | 0.2329 | 10.01 | 1 | 1 | R/X
5 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0.1908 | 0.31927 | 7.15 | 1 | 1 | R/X
5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
6 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.17273 | 0.1463 | 114.4 | 1 | 1 | R/X
6 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.18915 | 0.17474 | 85.8 | 1 | 1 | R/X
6 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.20785 | 0.2075 | 68.64 | 1 | 1 | R/X
6 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.2339 | 0.25671 | 52.91 | 1 | 1 | R/X
6 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.26261 | 0.31094 | 42.9 | 1 | 1 | R/X
6 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.29451 | 0.37119 | 34.32 | 1 | 1 | R/X
6 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.34308 | 0.4578 | 27.17 | 1 | 1 | R/X
6 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.43162 | 0.61733 | 20.02 | 1 | 1 | R/X
6 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 0 | 0.56782 | 0.87203 | 14.3 | 1 | 0 | R/X
6 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 0 | 0.72539 | 1.1645 | 10.01 | 0 | 0 | R/X
6 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 0 | 0.954 | 1.5963 | 7.15 | 0 | 0 | R/X
6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
7 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.040827 | 0.03458 | 57.2 | 1 | 1 | R/X
7 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.044707 | 0.041302 | 42.9 | 1 | 1 | R/X
7 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.049128 | 0.049045 | 34.32 | 1 | 1 | R/X
7 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.055286 | 0.060676 | 26.455 | 1 | 1 | R/X
7 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.062072 | 0.073494 | 21.45 | 1 | 1 | R/X
7 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.069611 | 0.087736 | 17.16 | 1 | 1 | R/X
7 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.081092 | 0.10821 | 13.585 | 1 | 1 | R/X
7 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.10202 | 0.14591 | 10.01 | 1 | 1 | R/X
7 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.13421 | 0.20612 | 7.15 | 1 | 1 | R/X
7 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0.17146 | 0.27525 | 5.005 | 1 | 1 | R/X
7 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0.22549 | 0.37731 | 3.575 | 1 | 1 | R/X
7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
8 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.28788 | 0.24383 | 114.4 | 1 | 1 | R/X
8 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.31524 | 0.29123 | 85.8 | 1 | 1 | R/X
8 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.34642 | 0.34583 | 68.64 | 1 | 1 | R/X
8 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.38983 | 0.42784 | 52.91 | 1 | 1 | R/X
8 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.43768 | 0.51823 | 42.9 | 1 | 1 | R/X
8 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.49085 | 0.61865 | 34.32 | 1 | 1 | R/X
8 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.5718 | 0.76299 | 27.17 | 1 | 1 | R/X
8 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.71937 | 1.0289 | 20.02 | 1 | 1 | R/X
8 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.94637 | 1.4534 | 14.3 | 1 | 1 | R/X
8 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 1.209 | 1.9408 | 10.01 | 0 | 0 | R/X
8 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 1.59 | 2.6605 | 7.15 | 0 | 0 | R/X
8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
9 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.21984 | 0.1862 | 114.4 | 1 | 1 | R/X
9 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.24073 | 0.2224 | 85.8 | 1 | 1 | R/X
9 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.26454 | 0.26409 | 68.64 | 1 | 1 | R/X
9 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.29769 | 0.32672 | 52.91 | 1 | 1 | R/X
9 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.33423 | 0.39574 | 42.9 | 1 | 1 | R/X
9 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.37483 | 0.47242 | 34.32 | 1 | 1 | R/X
9 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.43665 | 0.58265 | 27.17 | 1 | 1 | R/X
9 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.54934 | 0.78569 | 20.02 | 1 | 1 | R/X
9 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.72269 | 1.1099 | 14.3 | 1 | 1 | R/X
9 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0.92322 | 1.4821 | 10.01 | 1 | 1 | R/X
9 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 0 | 1.2142 | 2.0317 | 7.15 | 0 | 0 | R/X
9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
10 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.69091 | 0.5852 | 57.2 | 1 | 1 | R/X
10 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.75658 | 0.69896 | 42.9 | 1 | 1 | R/X
10 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.8314 | 0.82999 | 34.32 | 1 | 1 | R/X
10 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 0 | 0.9356 | 1.0268 | 26.455 | 1 | 0 | R/X
10 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 0 | 1.0504 | 1.2437 | 21.45 | 1 | 0 | R/X
10 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 0 | 1.178 | 1.4848 | 17.16 | 1 | 0 | R/X
10 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 0 | 1.3723 | 1.8312 | 13.585 | 1 | 0 | R/X
10 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 0 | 1.7265 | 2.4693 | 10.01 | 0 | 0 | R/X
10 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 0 | 2.2713 | 3.4881 | 7.15 | 0 | 0 | R/X
10 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 0 | 2.9015 | 4.658 | 5.005 | 0 | 0 | R/X
10 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 0 | 3.816 | 6.3853 | 3.575 | 0 | 0 | R/X
10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
11 | 400 | 520 | 0.22 | 0.1023 | 0.07 | 143 | 1 | 0.028178 | 0.023753 | 57.2 | 1 | 1 | R/X
11 | 300 | 447 | 0.27 | 0.13 | 0.071 | 143 | 1 | 0.030856 | 0.027936 | 42.9 | 1 | 1 | R/X
11 | 240 | 388 | 0.31 | 0.162 | 0.072 | 143 | 1 | 0.033907 | 0.032748 | 34.32 | 1 | 1 | R/X
11 | 185 | 325 | 0.41 | 0.211 | 0.072 | 143 | 1 | 0.038157 | 0.039926 | 26.455 | 1 | 1 | R/X
11 | 150 | 280 | 0.49 | 0.265 | 0.072 | 143 | 1 | 0.04284 | 0.047836 | 21.45 | 1 | 1 | R/X
11 | 120 | 247 | 0.57 | 0.325 | 0.072 | 143 | 1 | 0.048044 | 0.056624 | 17.16 | 1 | 1 | R/X
11 | 95 | 214 | 0.72 | 0.41 | 0.074 | 143 | 1 | 0.055968 | 0.069326 | 13.585 | 1 | 1 | R/X
11 | 70 | 173 | 1.05 | 0.567 | 0.077 | 143 | 1 | 0.070412 | 0.092699 | 10.01 | 1 | 1 | R/X
11 | 50 | 137 | 1.5 | 0.82 | 0.078 | 143 | 1 | 0.092631 | 0.12988 | 7.15 | 0 | 0 | R/X
11 | 35 | 115 | 2 | 1.11 | 0.08 | 143 | 1 | 0.11833 | 0.17261 | 5.005 | 0 | 0 | R/X
11 | 25 | 95 | 2.8 | 1.54 | 0.08 | 143 | 1 | 0.15563 | 0.2356 | 3.575 | 0 | 0 | R/X
11 | 16 | 73 | 4.5 | 1.54 | 0.08 | 143 | 1 | 0.15563 | 0.2356 | 2.288 | 0 | 0 | R/X
12 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0.001396 | 0.0011825 | 114.4 | 1 | 1 | R/X
12 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0.0015287 | 0.0013998 | 85.8 | 1 | 1 | R/X
12 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0.0016798 | 0.00165 | 68.64 | 1 | 1 | R/X
12 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0.0018904 | 0.0020243 | 52.91 | 1 | 1 | R/X
12 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0.0021224 | 0.0024368 | 42.9 | 1 | 1 | R/X
12 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0.0023802 | 0.0028951 | 34.32 | 1 | 1 | R/X
12 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0.0027728 | 0.0035559 | 27.17 | 1 | 1 | R/X
12 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0.0034884 | 0.0047724 | 20.02 | 1 | 1 | R/X
12 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.0045892 | 0.0067108 | 14.3 | 1 | 1 | R/X
12 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0.0058626 | 0.0089375 | 10.01 | 1 | 1 | R/X
12 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0.0077102 | 0.012222 | 7.15 | 1 | 1 | R/X
12 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
13 | 400 | 662.5 | 0.082 | 0.0602 | 0.07 | 143 | 1 | 0.00068349 | 0.00048426 | 127.9031 | 1 | 1 | R/X
13 | 300 | 568.8 | 0.104 | 0.0769 | 0.071 | 143 | 1 | 0.00073154 | 0.00055924 | 95.9273 | 1 | 1 | R/X
13 | 240 | 498.8 | 0.13 | 0.0965 | 0.072 | 143 | 1 | 0.0007866 | 0.00064668 | 76.7419 | 1 | 1 | R/X
13 | 185 | 421.2 | 0.169 | 0.127 | 0.072 | 143 | 1 | 0.00086032 | 0.00077773 | 59.1552 | 1 | 1 | R/X
13 | 150 | 365 | 0.212 | 0.159 | 0.072 | 143 | 1 | 0.00093766 | 0.00091523 | 47.9637 | 1 | 1 | R/X
13 | 120 | 321.2 | 0.26 | 0.196 | 0.072 | 143 | 1 | 0.0010271 | 0.0010742 | 38.3709 | 1 | 1 | R/X
13 | 95 | 276.2 | 0.328 | 0.247 | 0.074 | 143 | 1 | 0.0011657 | 0.0012998 | 30.377 | 1 | 1 | R/X
13 | 70 | 223.8 | 0.454 | 0.343 | 0.077 | 143 | 1 | 0.0014208 | 0.001722 | 22.383 | 1 | 1 | R/X
13 | 50 | 177.5 | 0.656 | 0.495 | 0.078 | 143 | 1 | 0.0017959 | 0.0023783 | 15.9879 | 1 | 1 | R/X
13 | 35 | 146.2 | 0.888 | 0.671 | 0.08 | 143 | 1 | 0.0022366 | 0.003141 | 11.1915 | 1 | 1 | R/X
13 | 25 | 120 | 1.232 | 0.93 | 0.08 | 143 | 1 | 0.0028626 | 0.0042539 | 7.9939 | 1 | 1 | R/X
13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
14 | 400 | 662.5 | 0.082 | 0.0602 | 0.07 | 143 | 1 | 0.00012151 | 8.609e-05 | 127.9031 | 1 | 1 | R/X
14 | 300 | 568.8 | 0.104 | 0.0769 | 0.071 | 143 | 1 | 0.00013005 | 9.942e-05 | 95.9273 | 1 | 1 | R/X
14 | 240 | 498.8 | 0.13 | 0.0965 | 0.072 | 143 | 1 | 0.00013984 | 0.00011497 | 76.7419 | 1 | 1 | R/X
14 | 185 | 421.2 | 0.169 | 0.127 | 0.072 | 143 | 1 | 0.00015295 | 0.00013826 | 59.1552 | 1 | 1 | R/X
14 | 150 | 365 | 0.212 | 0.159 | 0.072 | 143 | 1 | 0.0001667 | 0.00016271 | 47.9637 | 1 | 1 | R/X
14 | 120 | 321.2 | 0.26 | 0.196 | 0.072 | 143 | 1 | 0.00018259 | 0.00019097 | 38.3709 | 1 | 1 | R/X
14 | 95 | 276.2 | 0.328 | 0.247 | 0.074 | 143 | 1 | 0.00020724 | 0.00023108 | 30.377 | 1 | 1 | R/X
14 | 70 | 223.8 | 0.454 | 0.343 | 0.077 | 143 | 1 | 0.00025259 | 0.00030613 | 22.383 | 1 | 1 | R/X
14 | 50 | 177.5 | 0.656 | 0.495 | 0.078 | 143 | 1 | 0.00031927 | 0.00042281 | 15.9879 | 1 | 1 | R/X
14 | 35 | 146.2 | 0.888 | 0.671 | 0.08 | 143 | 1 | 0.00039763 | 0.0005584 | 11.1915 | 1 | 1 | R/X
14 | 25 | 120 | 1.232 | 0.93 | 0.08 | 143 | 1 | 0.00050891 | 0.00075625 | 7.9939 | 1 | 1 | R/X
14 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
15 | 400 | 662.5 | 0.082 | 0.0602 | 0.07 | 143 | 1 | 0.00019531 | 0.00013838 | 127.9031 | 1 | 1 | R/X
15 | 300 | 568.8 | 0.104 | 0.0769 | 0.071 | 143 | 1 | 0.00020904 | 0.0001598 | 95.9273 | 1 | 1 | R/X
15 | 240 | 498.8 | 0.13 | 0.0965 | 0.072 | 143 | 1 | 0.00022477 | 0.00018479 | 76.7419 | 1 | 1 | R/X
15 | 185 | 421.2 | 0.169 | 0.127 | 0.072 | 143 | 1 | 0.00024583 | 0.00022224 | 59.1552 | 1 | 1 | R/X
15 | 150 | 365 | 0.212 | 0.159 | 0.072 | 143 | 1 | 0.00026793 | 0.00026153 | 47.9637 | 1 | 1 | R/X
15 | 120 | 321.2 | 0.26 | 0.196 | 0.072 | 143 | 1 | 0.00029349 | 0.00030696 | 38.3709 | 1 | 1 | R/X
15 | 95 | 276.2 | 0.328 | 0.247 | 0.074 | 143 | 1 | 0.0003331 | 0.00037142 | 30.377 | 1 | 1 | R/X
15 | 70 | 223.8 | 0.454 | 0.343 | 0.077 | 143 | 1 | 0.000406 | 0.00049205 | 22.383 | 1 | 1 | R/X
15 | 50 | 177.5 | 0.656 | 0.495 | 0.078 | 143 | 1 | 0.00051317 | 0.0006796 | 15.9879 | 1 | 1 | R/X
15 | 35 | 146.2 | 0.888 | 0.671 | 0.08 | 143 | 1 | 0.00063912 | 0.00089754 | 11.1915 | 1 | 1 | R/X
15 | 25 | 120 | 1.232 | 0.93 | 0.08 | 143 | 1 | 0.000818 | 0.0012155 | 7.9939 | 1 | 1 | R/X
15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
16 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 3.7397e-05 | 3.1678e-05 | 127.9031 | 1 | 1 | R/X
16 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 4.0952e-05 | 3.75e-05 | 95.9273 | 1 | 1 | R/X
16 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 4.5001e-05 | 4.4202e-05 | 76.7419 | 1 | 1 | R/X
16 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 5.0641e-05 | 5.4229e-05 | 59.1552 | 1 | 1 | R/X
16 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 5.6857e-05 | 6.5279e-05 | 47.9637 | 1 | 1 | R/X
16 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 6.3764e-05 | 7.7558e-05 | 38.3709 | 1 | 1 | R/X
16 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 7.428e-05 | 9.5259e-05 | 30.377 | 1 | 1 | R/X
16 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 9.345e-05 | 0.00012785 | 22.383 | 1 | 1 | R/X
16 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0.00012294 | 0.00017977 | 15.9879 | 1 | 1 | R/X
16 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0.00015705 | 0.00023943 | 11.1915 | 1 | 1 | R/X
16 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0.00020655 | 0.00032742 | 7.9939 | 1 | 1 | R/X
16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manufacturer VD Ref
17 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
17 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
17 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
17 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
17 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
17 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
17 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
17 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
17 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
17 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
17 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
17 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
18 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
18 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
18 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
18 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
18 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
18 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
18 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
18 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
18 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
18 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
18 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
18 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
19 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
19 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
19 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
19 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
19 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
19 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
19 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
19 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
19 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
19 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
19 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
19 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
20 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
20 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
20 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
20 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
20 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
20 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
20 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
20 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
20 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
20 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
20 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
20 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
21 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
21 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
21 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
21 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
21 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
21 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
21 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
21 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
21 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
21 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
21 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
21 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
22 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
22 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
22 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
22 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
22 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
22 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
22 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
22 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
22 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
22 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
22 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
22 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
23 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
23 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
23 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
23 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
23 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
23 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
23 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
23 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
23 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
23 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
23 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
23 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
24 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
24 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
24 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
24 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
24 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
24 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
24 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
24 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
24 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
24 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
24 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
24 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
25 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
25 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
25 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
25 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
25 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
25 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
25 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
25 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
25 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
25 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
25 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
25 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
26 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
26 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
26 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
26 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
26 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
26 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
26 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
26 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
26 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
26 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
26 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
26 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
27 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
27 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
27 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
27 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
27 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
27 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
27 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
27 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
27 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
27 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
27 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
27 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
28 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
28 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
28 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
28 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
28 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
28 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
28 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
28 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
28 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
28 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
28 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
28 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
29 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
29 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
29 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
29 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
29 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
29 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
29 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
29 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
29 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
29 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
29 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
29 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
30 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
30 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
30 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
30 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
30 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
30 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
30 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
30 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
30 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
30 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
30 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
30 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
31 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
31 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
31 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
31 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
31 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
31 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
31 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
31 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
31 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
31 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
31 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
31 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
32 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
32 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
32 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
32 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
32 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
32 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
32 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
32 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
32 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
32 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
32 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
32 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
33 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
33 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
33 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
33 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
33 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
33 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
33 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
33 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
33 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
33 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
33 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
33 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
34 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
34 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
34 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
34 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
34 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
34 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
34 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
34 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
34 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
34 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
34 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
34 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
35 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
35 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
35 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
35 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
35 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
35 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
35 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
35 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
35 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
35 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
35 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
35 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
36 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
36 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
36 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
36 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
36 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
36 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
36 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
36 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
36 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
36 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
36 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
36 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
37 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
37 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
37 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
37 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
37 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
37 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
37 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
37 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
37 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
37 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
37 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
37 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
38 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
38 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
38 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
38 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
38 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
38 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
38 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
38 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
38 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
38 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
38 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
38 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
39 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
39 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
39 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
39 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
39 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
39 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
39 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
39 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
39 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
39 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
39 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
39 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
40 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
40 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
40 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
40 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
40 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
40 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
40 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
40 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
40 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
40 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
40 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
40 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
41 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
41 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
41 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
41 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
41 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
41 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
41 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
41 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
41 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
41 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
41 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
41 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
42 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
42 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
42 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
42 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
42 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
42 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
42 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
42 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
42 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
42 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
42 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
42 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
43 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
43 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
43 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
43 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
43 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
43 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
43 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
43 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
43 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
43 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
43 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
43 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
44 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
44 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
44 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
44 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
44 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
44 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
44 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
44 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
44 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
44 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
44 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
44 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
45 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
45 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
45 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
45 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
45 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
45 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
45 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
45 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
45 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
45 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
45 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
45 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
46 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
46 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
46 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
46 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
46 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
46 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
46 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
46 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
46 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
46 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
46 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
46 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
47 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
47 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
47 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
47 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
47 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
47 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
47 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
47 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
47 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
47 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
47 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
47 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
48 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
48 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
48 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
48 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
48 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
48 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
48 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
48 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
48 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
48 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
48 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
48 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
49 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
49 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
49 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
49 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
49 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
49 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
49 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
49 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
49 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
49 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
49 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
49 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
50 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
50 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
50 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
50 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
50 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
50 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
50 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
50 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
50 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
50 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
50 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
50 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
51 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
51 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
51 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
51 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
51 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
51 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
51 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
51 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
51 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
51 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
51 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
51 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
52 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
52 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
52 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
52 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
52 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
52 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
52 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
52 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
52 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
52 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
52 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
52 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
53 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
53 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
53 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
53 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
53 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
53 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
53 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
53 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
53 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
53 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
53 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
53 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
54 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
54 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
54 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
54 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
54 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
54 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
54 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
54 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
54 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
54 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
54 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
54 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
55 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
55 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
55 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
55 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
55 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
55 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
55 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
55 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
55 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
55 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
55 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
55 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
56 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
56 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
56 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
56 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
56 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
56 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
56 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
56 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
56 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
56 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
56 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
56 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
57 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
57 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
57 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
57 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
57 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
57 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
57 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
57 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
57 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
57 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
57 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
57 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
58 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
58 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
58 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
58 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
58 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
58 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
58 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
58 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
58 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
58 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
58 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
58 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
59 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
59 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
59 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
59 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
59 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
59 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
59 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
59 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
59 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
59 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
59 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
59 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
60 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
60 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
60 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
60 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
60 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
60 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
60 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
60 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
60 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
60 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
60 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
60 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
61 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
61 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
61 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
61 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
61 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
61 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
61 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
61 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
61 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
61 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
61 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
61 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
62 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
62 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
62 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
62 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
62 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
62 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
62 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
62 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
62 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
62 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
62 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
62 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
63 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
63 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
63 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
63 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
63 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
63 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
63 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
63 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
63 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
63 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
63 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
63 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
64 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
64 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
64 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
64 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
64 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
64 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
64 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
64 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
64 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
64 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
64 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
64 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
65 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
65 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
65 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
65 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
65 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
65 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
65 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
65 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
65 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
65 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
65 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
65 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
66 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
66 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
66 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
66 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
66 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
66 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
66 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
66 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
66 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
66 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
66 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
66 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
67 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
67 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
67 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
67 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
67 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
67 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
67 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
67 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
67 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
67 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
67 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
67 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
68 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
68 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
68 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
68 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
68 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
68 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
68 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
68 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
68 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
68 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
68 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
68 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
69 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
69 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
69 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
69 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
69 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
69 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
69 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
69 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
69 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
69 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
69 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
69 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
70 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
70 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
70 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
70 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
70 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
70 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
70 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
70 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
70 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
70 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
70 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
70 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
71 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
71 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
71 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
71 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
71 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
71 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
71 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
71 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
71 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
71 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
71 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
71 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
72 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
72 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
72 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
72 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
72 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
72 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
72 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
72 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
72 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
72 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
72 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
72 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
73 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
73 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
73 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
73 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
73 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
73 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
73 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
73 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
73 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
73 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
73 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
73 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
74 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
74 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
74 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
74 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
74 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
74 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
74 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
74 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
74 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
74 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
74 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
74 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
75 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
75 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
75 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
75 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
75 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
75 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
75 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
75 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
75 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
75 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
75 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
75 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
76 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
76 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
76 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
76 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
76 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
76 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
76 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
76 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
76 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
76 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
76 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
76 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
77 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
77 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
77 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
77 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
77 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
77 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
77 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
77 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
77 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
77 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
77 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
77 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
78 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
78 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
78 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
78 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
78 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
78 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
78 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
78 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
78 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
78 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
78 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
78 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
79 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
79 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
79 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
79 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
79 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
79 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
79 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
79 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
79 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
79 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
79 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
79 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
80 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
80 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
80 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
80 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
80 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
80 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
80 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
80 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
80 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
80 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
80 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
80 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
81 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
81 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
81 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
81 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
81 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
81 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
81 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
81 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
81 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
81 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
81 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
81 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
82 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
82 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
82 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
82 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
82 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
82 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
82 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
82 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
82 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
82 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
82 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
82 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
83 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
83 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
83 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
83 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
83 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
83 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
83 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
83 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
83 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
83 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
83 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
83 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
84 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
84 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
84 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
84 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
84 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
84 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
84 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
84 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
84 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
84 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
84 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
84 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
85 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
85 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
85 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
85 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
85 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
85 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
85 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
85 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
85 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
85 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
85 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
85 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
86 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
86 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
86 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
86 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
86 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
86 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
86 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
86 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
86 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
86 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
86 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
86 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
87 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
87 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
87 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
87 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
87 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
87 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
87 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
87 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
87 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
87 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
87 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
87 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
88 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
88 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
88 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
88 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
88 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
88 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
88 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
88 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
88 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
88 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
88 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
88 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
89 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
89 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
89 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
89 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
89 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
89 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
89 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
89 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
89 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
89 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
89 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
89 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
90 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
90 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
90 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
90 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
90 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
90 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
90 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
90 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
90 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
90 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
90 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
90 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
91 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
91 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
91 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
91 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
91 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
91 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
91 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
91 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
91 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
91 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
91 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
91 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
92 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
92 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
92 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
92 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
92 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
92 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
92 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
92 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
92 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
92 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
92 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
92 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
93 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
93 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
93 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
93 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
93 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
93 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
93 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
93 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
93 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
93 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
93 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
93 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
94 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
94 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
94 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
94 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
94 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
94 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
94 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
94 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
94 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
94 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
94 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
94 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
95 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
95 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
95 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
95 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
95 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
95 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
95 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
95 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
95 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
95 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
95 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
95 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
96 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
96 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
96 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
96 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
96 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
96 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
96 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
96 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
96 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
96 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
96 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
96 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
97 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
97 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
97 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
97 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
97 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
97 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
97 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
97 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
97 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
97 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
97 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
97 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
98 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
98 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
98 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
98 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
98 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
98 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
98 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
98 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
98 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
98 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
98 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
98 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
99 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
99 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
99 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
99 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
99 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
99 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
99 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
99 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
99 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
99 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
99 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
99 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
100 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
100 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
100 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
100 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
100 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
100 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
100 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
100 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
100 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
100 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
100 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
100 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
101 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
101 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
101 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
101 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
101 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
101 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
101 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
101 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
101 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
101 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
101 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
101 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
102 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
102 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
102 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
102 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
102 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
102 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
102 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
102 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
102 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
102 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
102 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
102 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref
103 | 400 | 530 | 0.1023 | 0.1023 | 0.07 | 143 | 1 | 0 | 0 | 127.9031 | 1 | 1 | R/X
103 | 300 | 455 | 0.13 | 0.13 | 0.071 | 143 | 1 | 0 | 0 | 95.9273 | 1 | 1 | R/X
103 | 240 | 399 | 0.162 | 0.162 | 0.072 | 143 | 1 | 0 | 0 | 76.7419 | 1 | 1 | R/X
103 | 185 | 337 | 0.211 | 0.211 | 0.072 | 143 | 1 | 0 | 0 | 59.1552 | 1 | 1 | R/X
103 | 150 | 292 | 0.265 | 0.265 | 0.072 | 143 | 1 | 0 | 0 | 47.9637 | 1 | 1 | R/X
103 | 120 | 257 | 0.325 | 0.325 | 0.072 | 143 | 1 | 0 | 0 | 38.3709 | 1 | 1 | R/X
103 | 95 | 221 | 0.41 | 0.41 | 0.074 | 143 | 1 | 0 | 0 | 30.377 | 1 | 1 | R/X
103 | 70 | 179 | 0.567 | 0.567 | 0.077 | 143 | 1 | 0 | 0 | 22.383 | 1 | 1 | R/X
103 | 50 | 142 | 0.82 | 0.82 | 0.078 | 143 | 1 | 0 | 0 | 15.9879 | 1 | 1 | R/X
103 | 35 | 117 | 1.11 | 1.11 | 0.08 | 143 | 1 | 0 | 0 | 11.1915 | 1 | 1 | R/X
103 | 25 | 96 | 1.54 | 1.54 | 0.08 | 143 | 1 | 0 | 0 | 7.9939 | 1 | 1 | R/X
103 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | Manufacturer VD Ref